SECTION 07 72 00

SOLAR POWER VENTILATOR

**This is a CSI Three-Part Specification using CSI MasterFormat 2004-2010 Section Numbers and Titles.  This specification must be edited to delete types of roof accessories not required on a particular project.  Also, for your guidance in editing this master guide specification we have put in **Notes** in asterisks’ and italicized to help guide you in your product selection.  You can then delete these notes once editing is completed.**

**This section is based on the Lomanco Incorporated line of roofing ventilation.   For more information on Lomanco Inc. products and availability, or for the name of your local Lomanco, Inc. representative, contact us at the following: Lomanco, Incorporated, 2101 West Main Street, P.O. Box 519, Jacksonville, Arkansas  72076, 1-800-643-5593 phone,                  
(501) 982-1258 fax; or visit our website at: www.lomanco.com.**

PART 1 - GENERAL

1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and 
		Supplementary Conditions and Division 01 Specification Sections, apply to 
		this Section.

1.2	SUMMARY

A.	Section Includes:

**Note: Delete roof accessories not used in project.**

1.	Solar power ventilators. **Note: Solar powered vents must be used in conjunction with adequate intake vents for proper operation.**

2.	Accessories.

B.	Related Sections:

**Note: Coordinate sections listed below with actual project requirements. **

1.	Section 07 31 13 - Asphalt Shingles

2.	Section 07 41 00 - Standing Seam Metal Roofing

3.	Section 07 51 13 - Built-Up Asphalt Roofing

4.	Section 07 52 13 - Modified Bituminous Membrane Roofing

5.	Section 07 53 23 - EPDM Roofing

6.	Section 07 54 19 - PVC Roofing

7.	Section 07 54 23 - TPO Roofing

8.	Section 07 61 00 - Sheet Metal Roofing

9.	Section 07 60 00 - Sheet Metal Flashing and Trim

10.	Section 07 71 00 - Roof Specialties

11.	Section 07 90 00 - Joint Sealants

1.3	REFERENCE STANDARDS

**Note: Delete unnecessary references not used in project.**

A.	American Society for Testing and Materials:

1.	ASTM B 209/B 209M - Specification for Aluminum and Aluminum-
			Alloy Sheet and Plate.

B.	National Fire Protection Association:

1.	NFPA 70 - National Electrical Code.

C.	Institute of Electrical and Electronics Engineers:

1.	IEEE C2 - National Electric Safety Code.

D.	Underwriters Laboratories Inc.:

1.	UL 1703 - Flat-Plate Photovoltaic Modules and Panels.

1.4	DESIGN/PERFORMANCE REQUIREMENTS

A.	General Performance: Solar powered ventilators shall withstand exposure to 
		weather and resist thermally induced movement without failure, rattling, 
		leaking, or fastener disengagement due to defective manufacture, fabrication, 
		installation, or other defects in construction.

B.	Design solar powered ventilators and components to be safe, normal 
		operation and designed and installed in accordance with manufacturer’s 
		written instructions and as designed on approved shop drawings, and in 
		compliance with applicable codes and jurisdictions.

1.5	QUALITY ASSURANCE

A.	Certification:

- CSA International: #253110.

- Passed Miami-Dade County test requirements for structural uplift 
and wind driven rain infiltration.  Miami-Dade County Approved - 
NOA No.: 12-0315.03 expires 06/14/2017.

3.	Texas Department of Insurance “Windstorm” Approved - Product 
			Evaluation Report No.: RV-68.

B.	Electrical Components, Devices, and Accessories:  Listed and labeled as 
		defined in NFPA 70, by a testing agency acceptable to authorities 
		having jurisdiction, and marked for intended use.

C.	Comply with NFPA 70.

D.	Comply with IEEE C2, “National Electrical Safety Code.”

E.	Comply with UL 1703.

1.6	ACTION SUBMITTALS

A.	Product Data: For solar power ventilator indicated.

1.7	INFORMATIONAL SUBMITTALS

A.	Coordination Drawings:

1.	Indicate locations of solar powered ventilator connections to utilities.

2.	Include plans and elevations; clearance requirements for access and 
			maintenance; details of supports; and utility service characteristics.

B.	Product Certificates: For specified solar power ventilator, from 
		manufacturer.

1.8	DELIVERY, STORAGE AND HANDLING

A.	Store products in manufacturer’s unopened packaging with labels intact 
		until ready for installation.

B.	Protect pipe openings and piping from debris and other foreign matter by 
		using caps on piping connections.

1.9	SEQUENCING

A.	Ensure that locating templates and other information required for 
		installation of products of this section are furnished to affected trades in time 
		to prevent interruption of construction progress.

1.10	COORDINATION

**Note: Coordinate with your project roofing requirements. **

A.	Coordinate layout and installation of solar power ventilator with roofing 
		membrane and base flashing and interfacing and adjoining construction to 
		provide a leakproof, weathertight, secure, and noncorrosive installation.

B.	Coordinate dimensions with rough-in information or Shop Drawings of 
		equipment to be supported.

1.11	WARRANTIES

A.	Manufacturer’s standard 10-year limited warranty for defects in 
		manufacturer’s materials and workmanship; 5-year warranty for ventilator 
		motor and panel.

PART 2 - PRODUCTS

2.1	MANUFACTURER

A.	Basis of Design: Lomanco, Incorporated, 2101 West Main Street, P.O.        
		Box 519, Jacksonville, Arkansas  72076, 1-800-643-5593 phone,                  
		(501) 982-1258 fax, www.lomanco.com is specified.

2.2	SOLAR POWER VENTILATOR

A.	Model “OSV-40 OMNI Solar Vent Power Ventilator”.

B.	Description: Self-flashing, roof mounted, solar-powered panel, attic exhaust 
		ventilator with one-piece dome, one-piece base, and one-piece 
		molded continuous rain shield/motor mount.  Double row of screen is secured 
		in place around rain shield and covers vent opening.

C.	Materials and Components:

1.	Aluminum: Conform to ASTM B 209.

a.	Base: 0.0305” aluminum coiled sheet.

b.	Dome: 0.051” aluminum coiled sheet.

c.	Fan Blade: 0.039” aluminum coiled sheet.

d.	Panel Mounting Brackets: 0.061” aluminum coiled sheet.

h.	Shaft: 0.500” diameter aluminum extrusion.

2.	Motor Mount/Rain Shield: High molecular terpolymer (ABS) with 
			UV stabilization additives.

3.	Solar Panel: 40 Watt, poly-crystalline silicon solar cell; comply with 
			UL 1703; National Electrical Code, NFPA 70; and National Safety 
			Electric Code, IEEE C2.

a.	Photovoltaic modules with maximum system voltage of         
				600 V dc and Class C fire rating.

4.	Motor: Fully enclosed, thermally protected, 24 Volt DC motor.

5.	Fan Blade: 5 blade design, stamped and formed as one-piece.

6.	Screen:  Manufacturer's standard, 16x18 aluminum mesh.

D.	Dimensions:  Overall 33.5” x 33.5” x 6.5”, Opening Size of 16”; Panel -      
		26” x 20.5”.

2.3	FINISHES:

A.	Comply with NAAMM's "Metal Finishes Manual for Architectural and 
		Metal Products" for recommendations for applying and designating finishes.

B.	Appearance of Finished Work:  Noticeable variations in same piece are not 
		acceptable.  Variations in appearance of adjoining components are 
		acceptable if they are within the range of approved Samples and are 
		assembled or installed to minimize contrast.

C.	Manufacturer’s standard “Valspar Super Flex” polyester coating with 
		minimum 0.8 top coat and minimum 0.3 wash coat.  Colors Available: 
		Brown, White, Black, Weathered Bronze.

PART 3 - EXECUTION

3.1	EXAMINATION

A.	Examine substrates, areas, and conditions, with Installer present, to verify 
		actual locations, dimensions, and other conditions affecting performance of 
		the Work.

B.	Verify that substrate is sound, dry, smooth, clean, sloped for drainage, and 
		securely anchored.

C.	Proceed with installation only after unsatisfactory conditions have been 
		corrected.

3.2	INSTALLATION

A.	General:  Install solar power ventilators according to manufacturer's written 
		instructions.

1.	Install solar power ventilators level, plumb, true to line and elevation, 
			and without warping, jogs in alignment, excessive oil canning, 
			buckling, or tool marks.

2.	Anchor ventilators securely in place so they are capable of 
			resisting indicated loads.

3.	Use fasteners, separators, sealants, and other miscellaneous items as 
			required to complete installation of ventilators and fit them to 
			substrates.

4.	Install ventilator to resist exposure to weather without failing, 
			rattling, leaking, or loosening of fasteners and seals.

B.	Metal Protection:  Protect metals against galvanic action by separating 
		dissimilar metals from contact with each other or with corrosive substrates 
		by painting contact surfaces with bituminous coating or by other permanent 
		separation as recommended by manufacturer.

1.	Coat concealed side of ventilator with bituminous coating 
			where in contact with wood, ferrous metal, or cementitious 
			construction.

2.	Underlayment:  Where installing ventilator directly on 
			cementitious or wood substrates, install a course of felt underlayment 
			and cover with a slip sheet, or install a course of polyethylene sheet.

3.	Bed flanges in thick coat of asphalt roofing cement where required by 
			manufacturer of ventilator for waterproof performance.

C.	Solar Power Ventilator Installation:  Verify that ventilators operate 
		properly and have unrestricted airflow.  Clean, lubricate, and adjust 
		operating mechanisms.

**Note: Coordinate type of sealant required with project requirements. **

D.	Seal joints with elastomeric or butyl sealant as required by solar 
		power ventilator manufacturer.  Comply with requirements of               
		Section 07 90 00 - Joint Sealants.

3.3	REPAIR AND CLEANING

**Note: Retain paragraph below for galvanized-steel surfaces. **

A.	Galvanized Surfaces:  Clean field welds, bolted connections, and abraded 
		areas and repair galvanizing according to ASTM A 780.

**Note: Retain paragraph below for primed surfaces. Coordinate section numbers with your project requirements**

B.	Touch up factory-primed surfaces with compatible primer ready for field 
		painting according to Section 09 91 13 - Exterior Painting and 
		Section 09 91 23 - Interior Painting.

C.	Clean exposed surfaces according to manufacturer's written instructions.

D.	Clean off excess sealants.

E.	Replace solar power ventilators that have been damaged or that cannot be 
		successfully repaired by finish touchup or similar minor repair procedures.

END OF SECTION